## Load list
Load | Working | Standby | kW each | pf | Efficiency | Load factor | Starting | Demand kW | Demand kvar
Process pumps | 3 | 1 | 75 | 0.86 | 0.94 | 0.8 | star-delta | 191.5 | 113.6
Air compressors | 1 | 1 | 160 | 0.88 | 0.95 | 0.85 | DOL | 143.2 | 77.3
Cooling tower fans | 4 | 0 | 22 | 0.84 | 0.91 | 0.8 | DOL | 77.4 | 50
Belt conveyors | 6 | 0 | 30 | 0.85 | 0.92 | 0.75 | DOL | 146.7 | 90.9
ID / FD fans | 2 | 0 | 110 | 0.95 | 0.95 | 0.8 | VFD | 185.3 | 60.9
Process heaters | 1 | 0 | 300 | 1 | 1 | 0.9 |  | 270 | 0
HVAC and chillers | 1 | 0 | 180 | 0.88 | 1 | 0.8 |  | 144 | 77.7
Lighting | 1 | 0 | 60 | 0.95 | 1 | 1 |  | 60 | 19.7
Workshop and small power | 1 | 0 | 80 | 0.85 | 1 | 0.5 |  | 40 | 24.8
Admin and utilities | 1 | 0 | 40 | 0.9 | 1 | 0.7 |  | 28 | 13.6
Total x diversity 0.9 | [7 empty] | 1157.4 | 475.6

## Sizing
Item | Value
Installed load | 1768 kW
Maximum demand | 1157 kW, 476 kvar, 1251 kVA at pf 0.925
With 20 % growth | 1502 kVA
Transformer (each) | 1600 kVA, 11/0.433 kV, Dyn11, uk 6.25 %, In 84.0 A HV / 2226 A LV
Loading today / with growth | 78 % / 94 %
Efficiency at today's load | 99.02 %
Regulation at today's load | 2.62 %
APFC to reach pf 0.95 | 95 kvar (detailed design: APFC project)
Largest DOL motor start (160 kW) | 1731 A, 5.8 % dip at the PCC

## Fault levels
Location | Ik (kA) | ip (kA) | pandapower Ik (kA)
11 kV bus, max | 18.37 | 45.36 | 18.37
11 kV bus, min | 13.12 | 32.4 | 13.12
415 V PCC, one transformer, max | 32.96 | 76.46 | 32.96
415 V PCC, one transformer, min | 28.2 | 65.47 | 28.2
415 V PCC, both paralleled (not allowed) | 61.2 | 142.58 | 61.2

## Switchgear
Item | Selected | Check
11 kV VCB | 12 kV, 630 A, 25 kA 3 s, making 62.5 kA peak | Ik 18.37 kA, ip 45.4 kA, DC time constant 31.8 ms (standard 45 ms)
11 kV busbar | 630 A | both transformers via one incomer: 168 A
11 kV cable to each transformer | 3C x 150 mm2 Al XLPE (UE) | fault withstand for backup clearing time governs, not current
LV incomer / bus coupler ACB | 2500 A, Ir 2250 A | transformer LV In 2226 A
LV PCC busbar | 2500 A, 50 kA 1 s, Icm 105 kA | Ik 33.0 kA, ip 76.5 kA; paralleled 61.2 kA exceeds rating, hence the interlock

## MV cable
Size (mm2) | Rating (A) | S min, main protection (mm2) | S min, backup protection (mm2) | OK
70 | 165 | 58.6 | 125.1 | FALSE
95 | 200 | 58.6 | 125.1 | FALSE
120 | 225 | 58.6 | 125.1 | FALSE
150 | 255 | 58.6 | 125.1 | TRUE
185 | 290 | 58.6 | 125.1 | TRUE
240 | 335 | 58.6 | 125.1 | TRUE

## Relay settings
Relay | CT | 51 pickup (A) | Curve | TMS | 50 pickup (A) | 50 delay (s)
Transformer feeder relay (TF1) | 150/1 | 138 | IEC EI | 0.68 | 1687 | 0.05
11 kV incomer relay (IN1) | 300/1 | 202 | IEC SI | 0.86 | 2193 | 0.35

## Grading
Pair | Current at 11 kV (A) | Downstream clears (s) | Upstream clears (s) | Margin (s)
LV incomer ACB -> TF1 (worst point) | 1297 | 0.38 | 0.684 | 0.304
LV incomer ACB -> TF1 at LV fault | 1297 | 0.38 | 0.684 | 0.304
TF1 -> IN1 (worst point) | 2207 | 0.11 | 0.41 | 0.3
TF1 highset -> IN1 at max 11 kV fault | 18370 | 0.09 | 0.41 | 0.32

## Checks
Check | Result
Faults on 11 kV cable / transformer HV cleared by | 0.09 s (TF1 + VCB)
11 kV bus faults cleared by | 0.41 s (IN1 delayed 50)
Curves that grade: TF1 / IN1 | VI, EI / SI
LV PCC fault cleared by LV incomer | 0.38 s
Backup by TF1 for the same fault | 0.68 s
Transformer through-fault withstand (IEC 60076-5) | 2.15 s
TF1 highset above inrush (12 x In, 0.1 s) | True
TF1 highset above 1.3 x reflected LV fault | True
TF1 highset below minimum 11 kV fault | True
CT effective ALF / linear up to | 69 / 10.3 kA (highset 1.69 kA)